## TABLE 4E2A and B
conductor cross-sectional area | TABLE 4E2A - Multicore 90 degrees celcius thermosetting insulated and thermoplastic sheathed cables, non-armoured (COPPER CONDUCTORS) | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8
CURRENT-CARRYING CAPACITY(amperes): Ambient temprature:30 degrees celcius Conductor operating temprature: 90 degrees celcius
| Reference method A (enclosed in conduit in thermally insulated wall etc.) |  | Reference method B (enclosed in conduit on a wall or in trunking etc.) |  | Reference method C (clipped direct) |  | Reference method E (free air or on a perforated cable tray etc, horizontal or vertical)
| 1 two-core cable* single phase a.c. or d.c. | 1 three-or four-core cable* three phase a.c. | 1 two-core cable* single-phase a.c or d.c | 1 three-or four-core cable* three-phase a.c. | 1 two-core cable* single phase a.c. or d.c. | 1 three-or four-core cable* three-phase a.c. | 1 two-core cable* single-phase a.c. or d.c. | 1 three or four-core cable* three-phase a.c.
(mm*2) | A | A | A | A | A | A | A | A
1 | 14.5 | 13 | 17 | 15 | 19 | 17 | 21 | 18
1.5 | 18.5 | 16.5 | 22 | 19.5 | 24 | 22 | 26 | 23
2.5 | 25 | 222 | 30 | 26 | 33 | 30 | 36 | 32
4 | 33 | 30 | 40 | 35 | 45 | 40 | 49 | 42
6 | 42 | 38 | 51 | 44 | 58 | 52 | 63 | 54
10 | 57 | 51 | 69 | 60 | 80 | 71 | 86 | 75
16 | 76 | 68 | 91 | 80 | 107 | 96 | 115 | 100
25 | 99 | 89 | 119 | 105 | 138 | 119 | 149 | 127
35 | 121 | 109 | 146 | 128 | 171 | 147 | 185 | 158
50 | 145 | 130 | 175 | 154 | 209 | 179 | 225 | 192
70 | 183 | 164 | 221 | 194 | 269 | 229 | 289 | 246
95 | 220 | 197 | 265 | 233 | 328 | 278 | 352 | 298
120 | 253 | 227 | 305 | 268 | 382 | 322 | 410 | 346
150 | 290 | 259 | 334 | 300 | 441 | 371 | 473 | 399
185 | 329 | 295 | 384 | 340 | 506 | 424 | 542 | 456
240 | 386 | 346 | 459 | 398 | 599 | 500 | 641 | 538
300 | 442 | 396 | 532 | 455 | 693 | 576 | 741 | 621
400 |  |  | 625 | 536 | 803 | 667 | 865 | 741

## TABLE 4E3A , 4E3B
Unnamed: 0 | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18
TABLE 4E3A – Single-core armoured 90 °C thermosetting insulated cables (non-magnetic armour) (COPPER CONDUCTORS)
CONDUCTOR CROSS SECTIONAL AREA | Reference Method C (clipped direct) |  | Reference Method F (in free air or on a perforated cable tray,horizontal or vertical)
| Touching |  | Touching |  |  | Spaced by one cable diameter | [6 empty] | Reference Methods C & F (clipped direct, on tray or in free air)
[6 empty] | 2 cables, d.c. |  | 2 cable, single-phase a.c. |  | 3 or 4 cables, three-phase a.c. |  |  |  | 2 cables, single-phase a.c. |  | 3 or 4 cables, three-phase a.c.
| 2 cables, singlephase a.c. or d.c. flat | 3 or 4 cables three phase a.c. flat | 2 cables, singlephase a.c. or d.c. flat | 3 cables three-phase a.c. flat | 3 cables three-phase a.c. trefoil | Horizontal | Vertical | Horizontal | Vertical | Horizontal | Vertical
[13 empty] | 2 cables, d.c. | touching | spaced* | trefoil and touching | flat and touching | flat and spaced*
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m)
(mm^2) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) |  |  | z | z | z | z | z
50 | 237 | 220 | 253 | 232 | 222 | 284 | 270 | 282 | 266 | 288 | 266 |  | 0.98 | 1 | 1 | 0.87 | 0.88 | 0.9
70 | 303 | 277 | 322 | 293 | 285 | 356 | 349 | 357 | 337 | 358 | 331 |  | 0.67 | 0.71 | 0.75 | 0.62 | 0.65 | 0.7
95 | 367 | 333 | 389 | 352 | 346 | 446 | 426 | 436 | 412 | 425 | 393 |  | 0.49 | 0.55 | 0.6 | 0.47 | 0.52 | 0.58
120 | 425 | 383 | 449 | 405 | 402 | 519 | 497 | 504 | 477 | 485 | 449 |  | 0.39 | 0.45 | 0.51 | 0.39 | 0.44 | 0.51
150 | 488 | 437 | 516 | 462 | 463 | 600 | 575 | 566 | 539 | 549 | 510 |  | 0.31 | 0.38 | 0.45 | 0.33 | 0.39 | 0.45
185 | 557 | 496 | 587 | 524 | 529 | 688 | 660 | 643 | 614 | 618 | 574 |  | 0.25 | 0.33 | 0.4 | 0.28 | 0.34 | 0.41
240 | 656 | 579 | 689 | 612 | 625 | 815 | 782 | 749 | 714 | 715 | 666 |  | 0.195 | 0.28 | 0.35 | 0.24 | 0.3 | 0.37
300 | 755 | 662 | 792 | 700 | 720 | 943 | 906 | 842 | 805 | 810 | 755 |  | 0.155 | 0.25 | 0.32 | 0.21 | 0.28 | 0.34
400 | 853 | 717 | 899 | 767 | 815 | 1137 | 1094 | 929 | 889 | 848 | 797 |  | 0.115 | 0.22 | 0.3 | 0.195 | 0.27 | 0.33
500 | 962 | 791 | 1016 | 851 | 918 | 1314 | 1266 | 1032 | 989 | 923 | 871 |  | 0.093 | 0.21 | 0.29 | 0.18 | 0.25 | 0.31
630 | 1082 | 861 | 1146 | 935 | 1027 | 1528 | 1474 | 1139 | 1092 | 992 | 940 |  | 0.073 | 0.195 | 0.27 | 0.17 | 0.24 | 0.29
800 | 1170 | 904 | 1246 | 987 | 1119 | 1809 | 1744 | 1204 | 1155 | 1042 | 978 |  | 0.056 | 0.19 | 0.27 | 0.165 | 0.23 | 0.26
1000 | 1261 | 961 | 1345 | 1055 | 1214 | 2100 | 2026 | 1289 | 1238 | 1110 | 1041 |  | 0.045 | 0.18 | 0.25 | 0.155 | 0.21 | 0.24
Conductor cross sectional area |  | Reference Methods C & F (clipped direct, on tray or in free air)
| 2 cables, d.c. | 2 cables, single-phase a.c. |  | 3 or 4 cables, three-phase a.c.
|  | touching | spaced* | trefoil and touching | flat and touching | flat and spaced*
| ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m) | ( mV/A/m)
|  | z | z | z | z | z
50 | 0.98 | 1 | 1 | 0.87 | 0.88 | 0.9
70 | 0.67 | 0.71 | 0.75 | 0.62 | 0.65 | 0.7
95 | 0.49 | 0.55 | 0.6 | 0.47 | 0.52 | 0.58
120 | 0.39 | 0.45 | 0.51 | 0.39 | 0.44 | 0.51
150 | 0.31 | 0.38 | 0.45 | 0.33 | 0.39 | 0.45
185 | 0.25 | 0.33 | 0.4 | 0.28 | 0.34 | 0.41
240 | 0.195 | 0.28 | 0.35 | 0.24 | 0.3 | 0.37
300 | 0.155 | 0.25 | 0.32 | 0.21 | 0.28 | 0.34
400 | 0.115 | 0.22 | 0.3 | 0.195 | 0.27 | 0.33
500 | 0.093 | 0.21 | 0.29 | 0.18 | 0.25 | 0.31
630 | 0.073 | 0.195 | 0.27 | 0.17 | 0.24 | 0.29
800 | 0.056 | 0.19 | 0.27 | 0.165 | 0.23 | 0.26
1000 | 0.045 | 0.18 | 0.25 | 0.155 | 0.21 | 0.24

## Table 4F1A
Unnamed: 0 | CURRENT-CARRYING CAPACITY (amperes) | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | VOLTAGE DROP (per ampere per metre) | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18
Conductor cross-sectional area | Single-phase a.c or d.c | Three-phase a.c | Single-pahse a.c or d.c |  | Two-core cable, dc |  | Two-core cable, single-phase a.c |  |  |  | 1 three-core, four-core or five-core cable, three-phase a.c |  |  |  | 2 single-core cables, touching
| 1 two-core cable, with or without protective conductor | 1 three-core, four-core or five-core cable | 2 single-core cables, touching | [11 empty] | d.c | Single-phase a.c
| (A) | (A) | (A) |  | (mV/A/m) |  |  | (mV/A/m) |  |  |  | (mV/A/m) |  |  |  |  | (mV/A/m)
4 | 30 | 26 | _ |  | 12 |  |  | 12 |  |  |  | 10 |  |  | _ |  | _
6 | 39 | 34 | _ |  | 7.8 |  |  | 7.8 |  |  |  | 6.7 |  |  | _ |  | _
10 | 51 | 47 | _ |  | 4.6 |  |  | 4.6 |  |  |  | 40 |  |  | _ |  | _
16 | 73 | 63 | _ |  | 2.9 |  |  | 2.9 |  |  |  | 2.5 |  |  | _ |  | _
[7 empty] | r | x | z |  | r | x | z |  |  | r | x | z
25 | 97 | 83 | _ |  | 1.8 |  | 1.8 | 0.175 | 1.85 |  | 1.55 | 0.15 | 1.55 |  | _ | _ | _ | _
35 | _ | 102 | 140 |  | _ |  | _ | _ | _ |  | 1.1 | 0.15 | 1.15 |  | 1.31 | 1.31 | 0.21 | 1.32
50 |  | 124 | 175 |  | _ |  | _ | _ | _ |  |  | 0.145 | 0.84 |  | 0.91 | 0.91 | 0.21 | 0.93
70 | _ | 158 | 216 |  | _ |  | _ | _ | _ |  |  | 0.14 | 0.58 |  | 0.64 | 0.64 | 0.2 | 0.67
95 | _ | 192 | 258 |  | _ |  | _ | _ | _ |  |  | 0.135 | 0.44 |  | 0.49 | 0.49 | 0.195 | 0.53
120 | _ | 222 | 302 |  | _ |  | _ | _ | _ |  |  | 0.135 | 0.36 |  | 0.38 | 0.38 | 0.19 | 0.43
150 | _ | 255 | 347 |  | _ |  | _ | _ | _ |  |  | 0.13 | 0.3 |  | 0.31 | 0.31 | 0.19 | 0.36
185 | _ | 291 | 394 |  | _ |  | _ | _ | _ |  |  | 0.13 | 0.26 |  | 0.25 | 0.25 | 0.19 | 0.32
240 | _ | 343 | 471 |  | _ |  | _ | _ | _ |  |  | 0.13 | 0.21 |  | 0.19 | 0.195 | 0.185 | 0.27
300 | _ | 394 | 541 |  | _ |  | _ | _ | _ |  | 0.135 | 0.125 | 0.185 |  | 0.15 | 0.155 | 0.18 | 0.24
400 | _ | _ | 644 |  | _ |  | _ | _ | _ |  | _ | _ | _ |  | 0.115 | 0.12 | 0.175 | 0.21
500 | _ | _ | 738 |  | _ |  | _ | _ | _ |  | _ | _ | _ |  | 0.09 | 0.099 | 0.17 | 0.2
630 | _ | _ | 861 |  | _ |  | _ | _ | _ |  | _ | _ | _ |  | 0.068 | 0.079 | 0.17 | 0.185

## TABLE 4F2A AND B
TABLE 4F2A _90 degrees celcius and 180 degrees celcius thermosetting insulated flexible cables with sheath, non-armoured (COPPER CONDUCTORS) CURRENT-CARRYING CAPACITY(amperes): Ambient temprature:30 degrees celcius Conductor operating temprature:90 degrees celcius | Unnamed: 1 | Unnamed: 2 | Unnamed: 3
Conductor cross- sectional area 1 | Single-phase a.c. or d.c. | Three - phase a.c. | Single-phase a.c. or d.c.
| 1 two-ore cables, with or without protective conductor 2 | 1 three-core four-core or five-core cable 3 | 2 single core cables, touching 4
(mm*2) | (A) | (A) | (A)
4 | 42 | 37
6 | 55 | 49
10 | 76 | 66
16 | 103 | 89
25 | 136 | 119
35 |  | 146 | 200
50 |  | 177 | 250
70 |  | 225 | 310
95 |  | 273 | 369
120 |  | 316 | 432
150 |  | 363 | 497
185 |  | 414 | 564
240 |  | 487 | 673
300 |  | 560 | 773
400 |  |  | 924
500 |  |  | 1062
630 |  |  | 1242

## table 4F3A, 473B
Unnamed: 0 | TABLE 4F3A - Flexible cables, non-armoured (COPPER CONDUCTORS) | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7
CURRENT-CARRYING CAPACITY (amperes): and MASS SUPPORTABLE (kg): | [5 empty] | VOLTAGE DROP (per ampere per metre):
|  | Current-carrying capacity |  | Maximum mass supportable by twin flexible cable (see Regulations 522.7.2 and 559.5.2) |  | d.c. or single-phase a.c. | Three-phase a.c.
| Conductor cross sectional area | Single-phase a.c. | Three-phase a.c. |  |  | (mV/A/m) | (mV/A/m)
| (mm2) | (A) | (A) | (kg)
| 0.5 | 3 | 3 | 2 |  | 93 | 80
| 0.75 | 6 | 6 | 3 |  | 62 | 54
| 1 | 10 | 10 | 5 |  | 46 | 40
| 1.25 | 13 | - | 5 |  | 37 | -
| 1.5 | 16 | 16 | 5 |  | 32 | 27
| 2.5 | 25 | 20 | 5 |  | 19 | 16
| 4 | 32 | 25 | 5 |  | 12 | 10

## Table 4G 1A,1B
Conductor cross-sectional area | CURRENT CARRYING CAPACITY | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | VOLTAGE DROP | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26
| Refernce Method C (clipped direct) |  |  | Reference Methods E, F and G (in free air or on a perforated cable tray etc, horizontal or vertical) |  |  |  |  | Single-phase a.c. or d.c. | [5 empty] | Three-phase a.c.
| Single-phase a.c. or d.c. | Three-phase a.c. |  | Single-phase a.c. or d.c. | Three-phase a.c. |  |  |  | 2 single-core cables touching |  |  | 1 two-core cable |  |  | 1 three or four-core cable |  |  | 3 single-core cables in trefoil formation |  |  | 3 single-core cables flat and touching |  |  | 3 single-core cables flat and spaced by one cable diameter
| 2 single-core cables touching or 1 two-core cable | 3 single-core cables in trefoil or 1 three-core or four-core cable | 3 single-core cables in trefoil or 1 three-core or four-core cable | 2 single-core touching or 1 two-core cable | 3 single-core cables in trefoil or 1 three-core or four-core cable | 3 single-core cables flat and touching | 3 single-core cables flat and spaced by one cable diameter
[7 empty] | vertical | horizontal
mm2 | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (mV/A/m) |  |  | (mV/A/m) |  |  | (mV/A/m) |  |  |  | (mV/A/m) |  | (mV/A/m) |  |  | (mV/A/m)
Light duty 500V
1 | 18.5 | 15 | 17 | 19.5 | 16.5 | 18 | 20 | 23
1.5 | 23 | 19 | 21 | 25 | 21 | 23 | 26 | 29
2.5 | 31 | 26 | 29 | 33 | 28 | 31 | 34 | 39
4 | 40 | 35 | 38 | 44 | 37 | 41 | 45 | 51
Heavy duty 750V
1 | 19.5 | 16 | 18 | 21 | 17.5 | 20 | 22 | 25 |  | 42 |  |  | 42 |  |  | 36 |  |  | 36 |  |  | 36 |  |  | 36
1.5 | 25 | 21 | 23 | 26 | 22 | 26 | 28 | 32 |  | 28 |  |  | 28 |  |  | 24 |  |  | 24 |  |  | 24 |  |  | 24
2.5 | 34 | 28 | 31 | 36 | 30 | 34 | 37 | 43 |  | 17 |  |  | 17 |  |  | 14 |  |  | 14 |  |  | 14 |  |  | 14
4 | 45 | 37 | 41 | 47 | 40 | 45 | 49 | 56 |  | 10 |  |  | 10 |  |  | 9.1 |  |  | 9.1 |  |  | 9.1 |  |  | 9.1
6 | 57 | 48 | 52 | 60 | 51 | 57 | 62 | 71 |  | 7 |  |  | 7 |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6
10 | 77 | 65 | 70 | 82 | 69 | 77 | 84 | 95 |  | 4.2 |  |  | 4.2 |  |  | 3.6 |  |  | 3.6 |  |  | 3.6 |  |  | 3.6
16 | 102 | 86 | 92 | 109 | 92 | 102 | 110 | 125 |  | 2.6 |  |  | 2.6 |  |  | 2.3 |  |  | 2.3 |  |  | 2.3 |  |  | 2.3
[9 empty] | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z
25 | 133 | 112 | 120 | 142 | 120 | 132 | 142 | 162 | 1.65 | 0.2 | 1.65 | 1.65 | 0.145 | 1.65 | 1.45 | 0.125 | 1.45 | 1.45 | 0.17 | 1.45 | 1.45 | 0.25 | 1.45 | 1.45 | 0.32 | 1.5
35 | 163 | 137 | 147 | 174 | 147 | 161 | 173 | 197 | 1.2 | 0.195 | 1.2 | _ | _ | _ | _ | _ | _ | 1.05 | 0.165 | 1.05 | 1.05 | 0.24 | 1.1 | 1.05 | 0.31 | 1.1
50 | 202 | 169 | 181 | 215 | 182 | 198 | 213 | 242 | 0.89 | 0.185 | 0.91 | _ | _ | _ | _ | _ | _ | 0.78 | 0.16 | 0.8 | 0.78 | 0.24 | 0.83 | 0.82 | 0.31 | 0.87
70 | 247 | 207 | 221 | 264 | 223 | 241 | 259 | 294 | 0.62 | 0.18 | 0.64 | _ | _ | _ | _ | _ | _ | 0.54 | 0.155 | 0.56 | 0.54 | 0.23 | 0.6 | 0.58 | 0.3 | 0.65
95 | 296 | 249 | 264 | 317 | 267 | 289 | 309 | 351 | 0.46 | 0.175 | 0.49 | _ | _ | _ | _ | _ | _ | 0.4 | 0.15 | 0.43 | 0.4 | 0.22 | 0.47 | 0.44 | 0.29 | 0.53
120 | 340 | 286 | 303 | 364 | 308 | 331 | 353 | 402 | 0.37 | 0.17 | 0.41 | _ | _ | _ | _ | _ | _ | 0.32 | 0.15 | 0.36 | 0.32 | 0.22 | 0.4 | 0.36 | 0.28 | 0.46
150 | 388 | 327 | 346 | 416 | 352 | 377 | 400 | 454 | 0.3 | 0.17 | 0.34 | _ | _ | _ | _ | _ | _ | 0.26 | 0.145 | 0.3 | 0.26 | 0.21 | 0.36 | 0.32 | 0.27 | 0.42
185 | 440 | 371 | 392 | 472 | 399 | 426 | 446 | 507 | 0.25 | 0.165 | 0.29 | _ | _ | _ | _ | _ | _ | 0.21 | 0.14 | 0.26 | 0.21 | 0.21 | 0.32 | 0.28 | 0.26 | 0.39
240 | 514 | 434 | 457 | 552 | 466 | 466 | 497 | 565 | 0.19 | 0.16 | 0.25 | _ | _ | _ | _ | _ | _ | 0.165 | 0.14 | 0.22 | 0.165 | 0.2 | 0.29 | 0.26 | 0.25 | 0.36

## TABLE4E1AB
Unnamed: 0 | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12
TABLE 4E1A - Single core thermosetting insulated cables , non armoured ,with or without sheath
COPPER CONDUCTORS
|  | Reference method A |  | Reference method B |  | Reference method C |  | Reference method F |  |  | Reference method G
| conductor cross-sectional | (Enclosed in conduit in thermally insulating wall |  | (Enclosed in conduit in thermally insulating wall or in trunking |  | Clipped direct |  | (in free air on a perforated cable tray etc horizontal or vertical etc) Touching |  |  | (in free air) spaced by one cable diameter
| area | 2 cables | 3 or 4 cables | 2 cables | 3 or 4 cables | 2 cables | 3 or 4 cables | 2 cables | 3 cables | 3 cables | 2 cables, single phase a.c or d.c or 3 cables , three phase a.c flat
|  | single phase a.c or d.c | three phase a.c | single phase a.c or d.c | three phase a.c | single phase a.c or d.c flat and touching | three phase a.c flat and touching or trefoil | single phase a.c or d.c flat | three phase a.c flat | three phase a.c trefoil | Horizontal | Vertical
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| mm2 | A | A | A | A | A | A | A | A | A | A | A
| 1 | 14 | 13 | 17 | 15 | 19 | 17.5 | - | - | - | - | -
| 1.5 | 19 | 17 | 23 | 20 | 25 | 23 | - | - | - | - | -
| 2.5 | 26 | 23 | 31 | 28 | 34 | 31 | - | - | - | - | -
| 4 | 35 | 31 | 42 | 37 | 46 | 41 | - | - | - | - | -
| 6 | 45 | 40 | 54 | 48 | 59 | 54 | - | - | - | - | -
| 10 | 61 | 54 | 75 | 66 | 81 | 74 | - | - | - | - | -
| 16 | 81 | 73 | 100 | 88 | 109 | 99 | - | - | - | - | -
| 25 | 106 | 95 | 133 | 117 | 143 | 130 | 161 | 141 | 135 | 182 | 161
| 35 | 131 | 117 | 164 | 144 | 176 | 161 | 200 | 176 | 169 | 226 | 201
| 50 | 158 | 141 | 198 | 175 | 228 | 209 | 242 | 216 | 207 | 275 | 246
| 70 | 200 | 179 | 253 | 222 | 293 | 268 | 310 | 279 | 268 | 353 | 318
| 95 | 241 | 216 | 306 | 269 | 355 | 326 | 377 | 342 | 328 | 430 | 389
| 120 | 278 | 249 | 354 | 312 | 413 | 379 | 437 | 400 | 383 | 500 | 454
| 150 | 318 | 285 | 393 | 342 | 476 | 436 | 504 | 464 | 444 | 577 | 527
| 185 | 362 | 324 | 449 | 384 | 545 | 500 | 575 | 533 | 510 | 661 | 605
| 240 | 424 | 380 | 528 | 450 | 644 | 590 | 679 | 634 | 607 | 781 | 719
| 300 | 486 | 435 | 603 | 514 | 743 | 681 | 783 | 736 | 703 | 902 | 833
| 400 | - | - | 683 | 584 | 868 | 793 | 940 | 868 | 823 | 1085 | 1008
| 500 | - | - | 783 | 666 | 990 | 904 | 1083 | 998 | 946 | 1253 | 1169
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1254 | 1151 | 1088 | 1454 | 1362
| 800 | - | - | - | - | 1288 | 1179 | 1358 | 1275 | 1214 | 1581 | 1485
| 1000 | - | - | - | - | 1443 | 1323 | 1520 | 1436 | 1349 | 1775 | 1671

## TABLE4E4A
Unnamed: 0 | Unnamed: 1 | TABLE4E4A-Multicore armoured 90 C thermosetting insulated cables | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8
|  |  | Reference method C (Clipped direct) |  | Reference Method E(in free air or on a perforated cable tray etc, horizontal or vertical) |  | Reference Method D (direct in ground or in ducting in ground, in or around buildings
|  |  | 1 two-core cable, single-phase a.c. or d.c. | 1 three - or four- core cable, three-phase a.c | 1 two-core cable, single-phase a.c or d.c | 1 three- or four-core cable, three-phase a.c | 1 two-core cable,single-phase a.c or d.c | 1 three- or four-core cable, three-phase a.c
|  | Conductor cross-sectional area | 2 | 3 | 4 | 5 | 6 | 7
(mm2) | bar: 2 to 7
|  | 1.5 | 27 | 23 | 29 | 25 | 25 | 21
|  | 2.5 | 36 | 31 | 39 | 33 | 33 | 28
|  | 4 | 49 | 42 | 52 | 44 | 43 | 36
|  | 6 | 62 | 53 | 66 | 56 | 53 | 44
|  | 10 | 85 | 73 | 90 | 78 | 71 | 58
|  | 16 | 110 | 94 | 115 | 99 | 91 | 75
|  | 25 | 146 | 124 | 152 | 131 | 116 | 96
|  | 35 | 180 | 154 | 188 | 162 | 139 | 115
|  | 50 | 219 | 187 | 228 | 197 | 164 | 135
|  | 70 | 279 | 238 | 291 | 251 | 203 | 167
|  | 95 | 338 | 289 | 354 | 304 | 239 | 197
|  | 120 | 392 | 335 | 410 | 353 | 271 | 223
|  | 150 | 451 | 386 | 472 | 406 | 306 | 251
|  | 185 | 515 | 441 | 539 | 463 | 343 | 281
|  | 240 | 607 | 520 | 636 | 546 | 395 | 324
|  | 300 | 698 | 599 | 732 | 628 | 446 | 365
|  | 400 | 787 | 673 | 847 | 728 | - | -
|  | Look up values For normal | 50 | 70 | 50 | 70 | 70 | 120
|  | Look up values For above normal | 50 | 120 | 95 | 120 | 185 | 300